|  |  |  |  |
| --- | --- | --- | --- |
| **Error number:** | **Text:** | **Cause:** | **Remedy:** |
| 1:2063 | TBI error 2063 Error during the function chdir | TBI can occur with the call AUTgetlinkedObjects. There should be an  AUT API tracer in the meantime. |  |

|  |  |  |  |
| --- | --- | --- | --- |
| **Error number:** | **Text:** | **Cause:** | **Remedy:** |
| 7:6160 | CPUs can only be connected via K bus or MPI bus  (line 1) |  | Split the desired path of the global data into several circuits. Make sure that  you only use on bus per circuit. |

|  |  |  |  |
| --- | --- | --- | --- |
| **Error number:** | **Text:** | **Cause:** | **Remedy:** |
| 11:103 | Cannot read CPU information on module, such as rated type, actual type and status of the module. Module might not be configured. |  | Check the logical address of the module. Check the slot and the configured slot. |

|  |  |  |  |
| --- | --- | --- | --- |
| **Error number:** | **Text:** | **Cause:** | **Remedy:** |
| 13:31 |  | The online connection from the PG to the module (SDB addressee) could not be set up. Connection hardware is faulty (e.g. connection cable removed). | Clear the fault in the connection to the module (SDB addressee) and you can then repeat the attempt to set up the connection in this dialog. |
|  | The online connection from the PG to the module (SDB addressee) could not be set up. The module (SDB addressee) is in the wrong operating mode. | Change the operating mode of the module (SDB addressee) and you can then repeat the attempt to set up the connection in this dialog. |
|  | The online connection from the PG to the module (SDB addressee) could not be set up. You have specified an incorrect MPI address with STEP 7. | If you have specified an incorrect MPI address, then:   1. Acknowledge this dialog 2. Correct the MPI address with STEP 7   Restart the "Load" function |